




         E N E R N E T Corporation

[image: image1.jpg]FAN COIL UNIT APELICATION NOTE:

The T8000 wireless RF thermostat with Plug-in Remote Control Node (RCN) can
quickly convert a FCU to precision, programmable temperature control:

1. Tum off power to the FCU atthe sircuit breaker.

2. Discomnectthe 110vac wiring feeding the fan spesd selector box

3. Install a standard 110vac receptacle using the FCU power wires.

4. Install a standard 110vac male plug with 3' of 14-gauge plug-cord on the fan spsed

selector box. (The cord s cannected where the wires in step 2 above were re-
moved)

Plug a 9000 Plug RN inta the newly installed receptale.

6. Plug the newly installed FCU male plug info the RCN and tum the FCU power
backon,

7. Tum the fan speed switch to the spesd you prefer.

8. Mount the T9000 thermostat in & sutable location and begin operating the FCU
from the themmastat

72000 Room
Thermostat
Adas
\
\
255, 4
Sy
A0
Wireless 7
R Link
FLOW VALVE NOTE:
Whether a 2-pipe or 4-pipe system, flow control valves
are typically powered though the ‘fan speed selector
switch. Cycling power as described will also work the
Fcu
flow valve in such configurations,

Fan Coil Retrofit

[ E—1
Sor]

e

Fan Speed
Selector Sw

(Typical 110vac Control Application)

OPTIONAL
FLOW VALVE

HI

=]
10| =
: Eﬂ
19000 Plug Standard
RON 110V Outiet

NOTES ENERNET Corporation 9000 Thesmmastet - Plog RO

13 T 000 ystem i i ey deve o R

‘contact between themostat and RCN. iihen installing the RCN, 07 Deyet sl Rupd

o 3 oo st ooty Srnded by st Speamuse, Neww Yod 13214 = T [
230t e he Py R e et f 15ami 3 11 (615) 490539 Y OICE. (15) 445-3056 FAX i

3.) Follow all National and local electrical wiring codes, practices, ik ot st
i i e





FAN COIL UNIT APPLICATION NOTE:


The T9000 wireless RF thermostat with Plug-in Remote Control Node (RCN) can quickly convert any 110vac FCU to precision, programmable temperature control:


Turn off power to the FCU at the circuit breaker.


Disconnect the 110vac wiring feeding the fan speed selector box.


Install a standard 110vac receptacle using the FCU power wires.


Install a standard 110vac 14-gauge plug-cord with male end on the fan speed selector box.  (The cord is connected where the wires in step 2 above were removed.)


Plug a T9000 Plug RCN into the newly installed receptacle.


Plug the newly installed FCU male plug into the RCN and turn the FCU power back on.


Turn the fan speed switch to the speed you prefer.


Mount the T9000 thermostat in a suitable location and begin operating the FCU from the thermostat.











FLOW VALVE NOTE:


Whether a 2-pipe or 4-pipe system, flow control valves are typically powered through the fan speed selector switch.  Cycling power as described will also work the flow valve in such configurations. 











NOTES:


1.) When installing, avoid locations that completely enclose the RCN behind sheet metal.


2.) Do not exceed the Plug RCN load rating of 15 amps at 110vac.


3.) Follow National and local electrical wiring codes, practices, guidelines and regulations.











Fan Coil Retrofit


(Typical 110vac Control Application)














T9000 Plug RCN











Standard 110V Outlet

















T9000 Room Thermostat











Fan Speed Selector Sw











E  N  E  R  N  E  T   C o r p o r a t i o n


307 Dewittshire Road


Syracuse, New York  13214


(315) 449-0839 VOICE   (315) 449-3056 FAX











T9000 Thermostat - Plug RCN











FCU





OPTIONAL FLOW VAVLE











Wireless


RF Link





PWR






























































     T9000 Plug-in Node Fan Coil Control Example



         http://www.enernetcorp.com

